## Residential
Fauquier County Water & Sanitation Authority Building 4176 Bludau Drive, Vint Hill Warrenton, VA 20187-1646 Telephone: (540) 349-2092 Fax: (540) 347-7689
Worksheet for Residential Water Meter Sizing
Subdivision Name / Lot # :
Customer / Builder Name :
Property Address :
Fixture | Unit Fixture Value | Number of Fixtures | Fixture Value
Bathtub | 8 |  | 0
Shower Head (Shower Only) | 2.5 |  | 0
Toilet, Tank Type | 4 |  | 0
Bathroom Sink (Lavatory) | 1.5 |  | 0
Kitchen Sink | 2.2 |  | 0
Wash Sink | 4 |  | 0
Dishwasher | 2 |  | 0
Washing Machine | 6 |  | 0
Hose Connection | 5 |  | 0
Other (Assign Unit Fixture Value) |  |  | 0
COMBINED FIXTURE VALUE |  |  | 0
Peak Domestic Demand |  |  | 0
Dedicated Irrigation Demand | Irrigated Area (SF) | Zones | Irrigation Demand
0
TOTAL FIXED DEMAND (Domestic plus Irrigation) |  |  | 0
REQUIRED WATER METER SIZE |  | 5/8 X 3/4 Inch

## Demand Table
Fixture Count | Residential Demand (gpm)
0 | 0
3 | 3
10 | 10
15 | 15
25 | 18
30 | 19
50 | 20
70 | 21
75 | 22
80 | 23
85 | 23
90 | 24
95 | 24
100 | 25
125 | 26
150 | 27
175 | 28
200 | 30
225 | 32
250 | 33
275 | 35
300 | 37
325 | 38
350 | 39
375 | 40
400 | 41
425 | 42
450 | 44
475 | 45
500 | 47
550 | 50
600 | 52
650 | 55
700 | 57
750 | 58
800 | 59
850 | 60
900 | 61
950 | 62
1000 | 63
1050 | 64
1100 | 65
1150 | 66
1200 | 67
1250 | 68
1300 | 69
1500 | 70
2000 | 75
3000 | 80
4000 | 85
5000 | 90
6000 | 95
7000 | 100
8000 | 105
9000 | 110
10000 | 115
11000 | 120
12000 | 125
13000 | 130